## Slide 1
Lift Station Service

## Slide 2
Above ground Vacuum Lift
Station

## Slide 3
Column pumps

## Slide 4
Dry well pumps

## Slide 5
Submersible pumps
Wet Well

## Slide 6
Types of submersible pumps
Non clog Vortex Grinders

## Slide 7
Main usages for submersible pumps
Waste water and storm water
Rail system Hard piped

## Slide 9
Main Components of a sump system
Pumps
Control Panel
Floats and / or transducer
Check Valves
ISO Valves
Rail System
Discharge Piping

## Slide 10
Why we would be called out to service a submersible pump
1. High Water Alarm
2. Breaker Tripped
Got remote alarm
Visual inspection
Compliant from customer - Water backing up
Remote monitoring – High amps, long run time
PM Service

## Slide 11
Check out the system
Visual look over the system Water level
Which Floats are tipped
Breakers and overloads
HOA Switches
Seal light and alarms
Voltage
Amps
Meg motor
Pump down
Rail system
Piping
Valves
2. Check Floats
3. Pull pump from sump

## Slide 12
Inspect breakers, overloads, and HOA switches
Overloads set to 1.25% of full load amps of pump
Seal fail light, high temp light, other alarms

## Slide 13
Check out the system
Visual look over the system Water level
Which Floats are tipped
Breakers and overloads
HOA Switches
Seal light and alarms
Voltage
Amps
Meg motor
Pump down
Rail system
Piping
Valves
2. Check Floats
3. Pull pump from sump

## Slide 14
Check incoming power and fuses

## Slide 15
Check moisture and thermal sensors
Red and Orange – Moisture Depends on pump
Black and White – Thermal Should have low ohm .2 – 1.5

## Slide 16
Check out the system
Visual look over the system Water level
Which Floats are tipped
Breakers and overloads
HOA Switches
Seal light and alarms
Voltage
Amps
Meg motor
Pump down
Rail system
Piping
Valves
2. Check Floats
3. Pull pump from sump

## Slide 17
Piggy back has 110VAC plug
Float tethered to pipe
Internal weight
External weight

## Slide 18
Check floats
Tip each float and check for light on controller
Ohm each float – Caution may have 110 VAC
Float down
Open
Float up
Closed
Check floats are hanging in correct order
Did pump Alternator Work
Clean all floats

## Slide 19
Check out the system
Visual look over the system Water level
Which Floats are tipped
Breakers and overloads
HOA Switches
Seal light and alarms
Voltage
Amps
Meg motor
Pump down
Rail system
Piping
Valves
2. Check Floats
3. Pull pump from sump

## Slide 20
Check for clog impeller

## Slide 21
Clog could be in pipe or valves
Check impeller clearance
Will reduce flow and clog easier

## Slide 22
Check oil
Inspect Power cord
Verify Pump Rotation

## Slide 23
If the pump need service
Close ISO Valve
Dewire pump
Tear down and inspect pump
Replace mech seals
Replace motor bearings
Pump Seals or O rings
Pump / Motor Oil
Reinstall Pump
Rewire pump
Check rotation
Install repaired pump
Make sure not to air lock pump
Open ISO valve
Check pump down
Check Amps